## Primary Venting
Dimensioning of venting in drainage systems type I (50% degree of filling) according to SS-EN 12056.
Refers to calculation for main line (Primary venting).
Project: |  |  |  |  | Performed by:
Property designation: |  |  |  |  | Date:
Designation of the main line:
PRIMARY VENTING |  |  | Number of sewage units connected:
|  | Number of levels: | - | 2 | 3 | 3 | -
Drain unit | Standard flow (l/s) |  | Basement level | Floor Type 1 | Floor Type 2 | Floor Type 3 | The attic
Washbasin, Bidet | 0.5 | → |  | 3
Shower cubicle without closable bottom valve | 0.6 | → |  | 2
Shower cubicle with closable bottom valve | 0.8 | →
Urinal with cistern | 0.8 | → |  |  | 1
Urinal with flush valve | 0.5 | →
Urinal through | 0.2 | → |  |  | 2
Bathtub | 0.8 | →
Sink | 0.8 | → |  | 2
Dishwasher (Household) | 0.8 | →
Washing machine 6 Kg | 0.8 | → |  |  | 3
Washing machine 12 Kg | 1.5 | →
Water closet 6 l | 2 | → |  | 2
Water closet 9 l | 2.5 | →
Floor gullies DN 50 | 0.8 | →
Floor gullies DN 70 | 1.5 | →
Floor gullies DN 100 | 2 | →
Other device: |  | →
Other device: |  | →
Other device: |  | →
Summed standard flow (l/s): |  |  | 0 | 16.6 | 10.8 | 0 | 0
Summed Standard flow for the main line (l/s): | 27.4
Frequency factor K: | 0.5 | → | Frequency factor is chosen according to the area of ​​use |  | Area of application |  | K
Expected flow Qww (l/s): | 2.6173 |  |  |  | Intermittent operation (Residential, Office, etc.) |  | 0.5
Supplied continuous flow Qc (l/s): | 0 |  |  |  | Frequent operations (Hospitals, Schools, Hotels, etc.) |  | 0.7
Supplied pumped flow Qp (l/s): | 0 |  |  |  | Continuous operation (Public toilets, etc.) |  | 1
Total flow Qtot (l/s): | 2.6173 | Which air admittance valve should I choose? |  |  | Specific conditions (Laboratory, etc.) |  | 1.2
Required capacity of vent valve Qa (l/s): | 20.938 | 3131160
(For main line: Qa = 8 x Qtot)
Flow | RSK (article)
0-11,3 l/s = | 3131162 (50/40), 3131164 (40-adapter) , 3131166 (40)
11,4-35 l/s = | 3131160 (75)
35,1-78 l/s = | 3131161 (110)

## Secondary Venting
Dimensioning of venting in drainage systems type I (50% filling level) according to SS-EN 12056.
Refers to calculation for connecting line (secondary venting).
Project: |  |  |  | Date:
Property designation: |  |  |  | Performed by:
Designation of the line:
SECONDARY VENTING
Drain unit | Normal flow (l/s) |  | Number
Washbasin, Bidet | 0.5 | → | 2
Shower cubicle without closable bottom valve | 0.6 | → | 1
Shower cubicle with closable bottom valve | 0.8 | →
Urinal with cistern | 0.8 | →
Urinal with flush valve | 0.5 | →
Urinal through | 0.2 | →
Bathtub | 0.8 | →
Sink | 0.8 | →
Dishwasher (Household) | 0.8 | →
Washing machine 6 Kg | 0.8 | → | 1
Washing machine 12 Kg | 1.5 | →
Water closet 6 l | 2 | → | 1
Water closet 9 l | 2.5 | →
Floor gullies DN 50 | 0.8 | →
Floor gullies DN 70 | 1.5 | → | 1
Floor gullies DN 100 | 2 | →
Other device: |  | →
Other device: |  | →
Other device: |  | →
Summed standard flow (l/s): |  |  | 5.9
Supplied continuous flow Qc (l/s): |  |  | 0
Supplied pumped flow Qp (l/s): |  |  | 0
Total flow Qtot (l/s): |  |  | 5.9
Required capacity of vent valve Qa (l/s): |  |  | 5.9 | (For connected line: Qa = 1 x Qtot)
Flow | RSK-article
0-11 l/s = | 3131162, 3131164, 3131166
11,1-35 l/s = | 3131160
35,1-78 l/s = | 3131161