## Slide 1: LINCNODE installation and COMMISSIONING training
Alexander V. klekachev

## Slide 2: Outline
Lincnode introduction
Lincnode installation
Commissioning process
Commissioning tool operation

## Slide 3: Lincnode introduction (1)
. . .
Small form-factor IoT gateway
Monitoring data from ADB Safegate CCR regulators
Uses cellular network to transfer data to the cloud
Supports MODBUS RTU (RS485) and MODBUS TCP connections
Supports MCR2 and MCR3 MODBUS protocols
Supports CRE and MCR3 CCRs
Cloud services
Modbus interface
GSM, LTE CAT-M1, NB-IOT

## Slide 4: Lincnode introduction (2)
Power connector
Micro-USB
Cellular antenna connector
Status LED
Ethernet version
Serial version
Micro-USB

## Slide 5: Lincnode installation (1)
Power cable
Antenna
DIN rail
clips (2x)
Mounting bracket
Power supply (not shown)

## Slide 6: Lincnode installation (2)

## Slide 7: Lincnode installation (3)
Power supply
Circuit breaker

## Slide 8: Commissioning process (1)
Install the Lincnode device following the instructions
Perform all necessary connections between the CCRs and the device
  In case of Serial device, make daisy-chained RS485 connections of CCRs (up to 16 CCRs supported)
  In case of Ethernet device, use Ethernet switch to connect the Lincnode with the CCRs (up to 4 CCRs supported)
Power Lincnode device
Connect Lincnode device to the PC using micro-USB cable
Start the Commissioning Tool application

## Slide 9
One must enable the termination of the RS485 interface at the very last unit in the daisy-chained net
  Follow the instructions for a particular CCR on how to set the termination
Additionally, termination needs to be enabled in the Lincnode device
  This is achieved via Commissioning Tool software
RS485 interface
Commissioning process (1): Serial device details

## Slide 10: Commissioning Tool key steps
Check cellular connectivity status:
  Shows whether device is registered on the network
Configure the Modbus interface:
  In case of Serial device set RS485 parameters
  In case of Ethernet device set the IP Address and mask (CIDR format)
Configure Modbus assets (CCRs):
  Define CCR protocol
  Define CCR RTU addresses, in case of Ethernet, IP Address and Port
  Add as many CCRs as necessary.
Apply device configuration
  Device Modbus interface and assets information gets transferred to the device

## Slide 11: Account selection screen
When starting the application, it will invite you to login into your ADB Safegate account.

## Slide 12: Commissioning Tool: dashboard (Ethernet version)
Cellular connectivity status overview
Modbus assets summary
Device hardware identity
Modbus interface settings
Device configuration status

## Slide 13: Commissioning Tool: dashboard (Serial version)
Cellular connectivity status overview
Modbus assets summary
Device hardware identity
Modbus interface settings
Device configuration status
Termination resistor

## Slide 14: Commissioning Tool: cellular status monitoring
Status LED

## Slide 15
Status LED: amber color
Status LED: red color

## Slide 16: Commissioning Tool: Modbus assets (Ethernet)

## Slide 17: Commissioning Tool: Modbus assets (Serial)

## Slide 18: Commissioning Tool: apply configuration
When all parameters set press “APPLY CONFIG” button.

## Slide 19: Commissioning Tool: save screenshot of this view (for ALIS)

## Slide 20: That’s all folks!