## Vault Heat Calculation
Airport Information
Airport:
Vault:
DEVICE | QTY | HEAT LOSS (WATTS) | BTU/HR GENERATED | TOTAL BTU/HR | COMMENTS
Advanced Power Supply
APS - 1kW (90% Efficient) |  | 100 | 341.3 | 0
APS - 2kW (90% Efficient) |  | 200 | 682.6 | 0
Constant Current Regulators
CCR - 2.5kW (90% Efficient) |  | 250 | 853.25 | 0
CCR - 4kW (90% Efficient) |  | 400 | 1365.2 | 0
CCR - 5kW (90% Efficient) |  | 500 | 1706.5 | 0
CCR - 7.5kW (90% Efficient) |  | 750 | 2559.75 | 0
CCR - 10kW (90% Efficient) |  | 1000 | 3413 | 0
CCR - 15kW (90% Efficient) |  | 1500 | 5119.5 | 0
CCR - 20kW (90% Efficient) |  | 2000 | 6826 | 0
CCR - 25kW (90% Efficient) |  | 2500 | 8532.5 | 0
CCR - 30kW (92% Efficient) |  | 2400 | 8191.2 | 0
CCR - 50kW (93% Efficient) |  | 3500 | 11945.5 | 0
CCR - 70kW (94% Efficient) |  | 4200 | 14334.6 | 0
ACE Distributed Control Units
ACE 1 |  | 15 | 51.195 | 0
ACE 2 |  | 12 | 40.956 | 0
ACE 3 |  | 12 | 40.956 | 0
Other
L-854 Radio Controller (ADB) |  | 15 | 51.195 | 0
L-847 Circuit Selector (1 Switch) |  | 150 | 511.95 | 0
L-847 Circuit Selector (2 Switches) |  | 160 | 546.08 | 0
L-847 Circuit Selector (3 Switches) |  | 170 | 580.21 | 0
L-847 Circuit Selector (4 Switches) |  | 180 | 614.34 | 0
L-884 LAHSO Power Controller |  | 160 | 546.08 | 0
BRITE II or AGLAS C Master |  | 300 | 1023.9 | 0
LINC 360 Controller |  | 300 | 1023.9 | 0
ALSF Control Cbainet |  | 300 | 1023.9 | 0
ALCMS Airfield Lighting Systems
ALCMS Industrial PC |  | 250 | 853.25 | 0
ALCMS LCD Monitor 17" |  | 32 | 109.216 | 0
ALCMS LCD Monitor 19" |  | 35 | 119.455 | 0
ALCMS LCD Monitor 21" |  | 75 | 255.975 | 0
APC UPS- 750 VA |  | 19.9 | 67.9187 | 0
APC UPS- 1,000 VA |  | 26 | 88.738 | 0
APC UPS- 1,500 VA |  | 50.1 | 170.9913 | 0
APC UPS- 2,200 VA |  | 80.57 | 274.9854 | 0
APC UPS- 3,000 VA |  | 109.87 | 374.9863 | 0
People
People (if normally occupied) |  | 400 | 1365.2 | 0
|  |  | TOTAL: | 0 | BTU/HR
|  |  |  | 0 | Tons AC Required
VAULT HEAT GENERATION CALCULATOR ¦ © 2009-2023 ADB SAFEGATE ¦ All Rights Reserved.